## power_meter
SN | Signal Name | Tag Name (Sanitized) | Read/ Write | Type | Unit | Gain | Address | Quantity
1 | Phase A voltage | 1_PHASE_A_VOLTAGE | r | uint32 | V | 100 | 32260 | 2
2 | Phase B voltage | 2_PHASE_B_VOLTAGE | r | uint32 | V | 100 | 32262 | 2
3 | Phase C voltage | 3_PHASE_C_VOLTAGE | r | unit32 | V | 100 | 32264 | 2
4 | A-B line voltage | 4_AB_LINE_VOLTAGE | r | uint32 | V | 100 | 32266 | 2
5 | B-C line voltage | 5_BC_LINE_VOLTAGE | r | uint32 | V | 100 | 32268 | 2
6 | C-A line voltage | 6_CA_LINE_VOLTAGE | r | uint32 | V | 100 | 32270 | 2
7 | Phase A current | 7_PHASE_A_CURRENT | r | int32 | A | 10 | 32272 | 2
8 | Phase B current | 8_PHASE_B_CURRENT | r | int32 | A | 10 | 32274 | 2
9 | Phase C current | 9_PHASE_C_CURRENT | r | int32 | A | 10 | 32276 | 2
10 | Active power | 10_ACTIVE_POWER | r | int32 | kW | 1000 | 32278 | 2
11 | Reactive power | 11_REACTIVE_POWER | r | int32 | kVar | 1000 | 32280 | 2
12 | Active electricity(Reserved) | 12_ACTIVE_ELECTRICITYRESERVED | r | int32 | kWh | 10 | 32282 | 2
13 | Power factor | 13_POWER_FACTOR | r | int16 | N/A | 1000 | 32284 | 1
14 | Reactive electricity(Reserved) | 14_REACTIVE_ELECTRICITYRESERVED | r | int32 | kvarh | 10 | 32285 | 2
15 | Apparent power | 15_APPARENT_POWER | r | int32 | kVA | 1000 | 32287 | 2
16 | Positive active electricity(Reserved) | 16_POSITIVE_ACTIVE_ELECTRICITYRESERVED | r | int32 | kWh | 100 | 32289 | 2
17 | Positive reactive electricity(Reserved) | 17_POSITIVE_REACTIVE_ELECTRICITYRESERVED | r | int32 | kvarh | 100 | 32291 | 2
18 | Electricity in positive active electricity price segment 1 | 18_ELECTRICITY_IN_POSITIVE_ACTIVE_ELECTRICITY_PRICE_SEGMENT_1 | r | int32 | kWh | 100 | 32299 | 2
19 | Electricity in positive active electricity price segment 2 | 19_ELECTRICITY_IN_POSITIVE_ACTIVE_ELECTRICITY_PRICE_SEGMENT_2 | r | int32 | kWh | 100 | 32301 | 2
20 | Electricity in positive active electricity price segment 3 | 20_ELECTRICITY_IN_POSITIVE_ACTIVE_ELECTRICITY_PRICE_SEGMENT_3 | r | int32 | kWh | 100 | 32303 | 2
21 | Electricity in positive active electricity price segment 4 | 21_ELECTRICITY_IN_POSITIVE_ACTIVE_ELECTRICITY_PRICE_SEGMENT_4 | r | int32 | kWh | 100 | 32305 | 2
22 | Electricity in negative active electricity price segment 1 | 22_ELECTRICITY_IN_NEGATIVE_ACTIVE_ELECTRICITY_PRICE_SEGMENT_1 | r | int32 | kWh | 100 | 32307 | 2
23 | Electricity in negative active electricity price segment 2 | 23_ELECTRICITY_IN_NEGATIVE_ACTIVE_ELECTRICITY_PRICE_SEGMENT_2 | r | int32 | kWh | 100 | 32309 | 2
24 | Electricity in negative active electricity price segment 3 | 24_ELECTRICITY_IN_NEGATIVE_ACTIVE_ELECTRICITY_PRICE_SEGMENT_3 | r | int32 | kWh | 100 | 32311 | 2
25 | Electricity in negative active electricity price segment 4 | 25_ELECTRICITY_IN_NEGATIVE_ACTIVE_ELECTRICITY_PRICE_SEGMENT_4 | r | int32 | kWh | 100 | 32313 | 2
26 | Custom 1 | 26_CUSTOM_1 | r | int32 | N/A | 1000 | 32315 | 2
27 | Custom 2 | 27_CUSTOM_2 | r | int32 | N/A | 1000 | 32317 | 2
28 | Custom 3 | 28_CUSTOM_3 | r | int32 | N/A | 1000 | 32319 | 2
29 | Custom 4 | 29_CUSTOM_4 | r | int32 | N/A | 1000 | 32321 | 2
30 | Custom 5 | 30_CUSTOM_5 | r | int32 | N/A | 1000 | 32323 | 2
31 | Custom 6 | 31_CUSTOM_6 | r | int32 | N/A | 1000 | 32325 | 2
32 | Custom 7 | 32_CUSTOM_7 | r | int32 | N/A | 1000 | 32327 | 2
33 | Custom 8 | 33_CUSTOM_8 | r | int32 | N/A | 1000 | 32329 | 2
34 | Custom 9 | 34_CUSTOM_9 | r | int32 | N/A | 1000 | 32331 | 2
35 | Custom 10 | 35_CUSTOM_10 | r | int32 | N/A | 1000 | 32333 | 2
36 | Phase A active power | 36_PHASE_A_ACTIVE_POWER | r | int32 | kW | 1000 | 32335 | 2
37 | Phase B active power | 37_PHASE_B_ACTIVE_POWER | r | int32 | kW | 1000 | 32337 | 2
38 | Phase C active power | 38_PHASE_C_ACTIVE_POWER | r | int32 | kW | 1000 | 32339 | 2
39 | Total active electricity | 39_TOTAL_ACTIVE_ELECTRICITY | r | int64 | kWh | 100 | 32341 | 4
40 | Total reactive electricity | 40_TOTAL_REACTIVE_ELECTRICITY | r | int64 | kvarh | 100 | 32345 | 4
41 | Negative active electricity | 41_NEGATIVE_ACTIVE_ELECTRICITY | r | int64 | kWh | 100 | 32349 | 4
42 | Negative reactive electricity | 42_NEGATIVE_REACTIVE_ELECTRICITY | r | int64 | kvarh | 100 | 32353 | 4
43 | Positive active electricity | 43_POSITIVE_ACTIVE_ELECTRICITY | r | int64 | kWh | 100 | 32357 | 4
44 | Positive reactive electricity | 44_POSITIVE_REACTIVE_ELECTRICITY | r | int64 | kvarh | 100 | 32361 | 4